## Fault Sheet
BOTSWANA POWER CORPORATION
FAULT NO: | 060/22
DAY/DATE | Monday 25 February 2024 | WEATHER | CLEAR | VOLTAGE LEVEL | 132/11k | AREA: | South
TIME | APPARATUS TRIPPED | PROTECTION INDICATIONS |  | TIME RECLOSED | REPORTED BY | BREAKER SEQUENCE
| Gab East 132/11 kV T1B : HV CB 110B | did not trip
| : LV CB 1H0B | did not trip
12h52 | Gab East 132/11 kV T1A : HV CB 110A | O/C & E/F : A & B To Ground |  | 14h08 | SCADA/R. Galetshets | Tripped
| : LV CB 1H0A | O/C & E/F : A & B To Ground |  | 14h14 | SCADA/R. Galetshets | Tripped
OPERATIONS CARRIED OUT
CSS requested to close one feeder at a time and 132/11 kV Transformer 1A closed first and Transformer 2A followed and they both held.
LINE INSPECTION ETC
CSS advised fault was due to one of the feeders CB failed to trip during fault, hence through fault.